## Comparison of Flow
Comparison | [6 empty] | Propsed as per the revised P&ID
|  | PCB | PROJECT | PROJECTION |  |  | P&ID
[5 empty] | ETP | KLD | STREAM-01 (Heavy Metal Waste water)
1 | WTP | 3372.5 | 7000 | 1 | Heavy Metal Waste water | 207 | 1 | Nickel liquid | 11.52 | 206.51
|  |  |  | 2 | High con Phosphrous Waste water | 642 | 2 | Nickel water rinsing | 194.99
2 | STP | 638.8 | 1200 | 3 | Comprehensive Waste water | 741
|  |  |  | 4 | VI Cleaning Water | 505 | STREAM-02
3 | ETP-1 |  |  | 5 | Waste Liquid minimization | 65 | 3 | Washing water | 50 | 285.94
| ETP-2 | 8943.8 | 10539 | 6 | Organic Waste water | 2759 | 4 | Phosphoric WW | 235.94
|  |  |  | 7 | Zero Liquid Discharge system | 5620
STREAM-03 (Waste Liquid minimization)
4 | DM-1 |  |  |  | TOTAL | 10539 | 5 | Waste scraping water | 9.6 | 64.74
| DM-2 | 4693 | 4153 |  |  |  | 6 | Coolant | 9.6
[5 empty] | WTP | 7000 | 7 | Oraganic bath solution | 7.82
[5 empty] | DI | 4153 | 8 | VI Waste dip bath liquid | 24.17
[7 empty] | 9 | Dyeing bath liquid | 13.55
STREAM-04
[7 empty] | 10 | VI Rinsing WW | 30.77 | 170.12
[7 empty] | 11 | VI Rinsing WW | 139.35
STREAM-05 (Comprehensive Waste water )
[7 empty] | 12 | Waste acid liquid | 14.12 | 740.91
[7 empty] | 13 | Comprehensive acid WW | 440.8
[7 empty] | 14 | Waste Alkali liquid | 3.58
[7 empty] | 15 | Comprehensive alkali WW | 282.41
STREAM-06
[7 empty] | 16 | Organic rinsing water | 188.73 | 3328.3
[7 empty] | 17 | Organic other rinsing water | 1357.85
[7 empty] | 18 | WTP reject | 18
[7 empty] | 19 | DI concentrated water | 1744.62
[7 empty] | 20 | Boiler waste liquid | 19.08
[9 empty] | 4796.5 | 4796.52

## Requirement
Requirement
1 | WTP
i | Rectangular tank with Submerged Scrapper- T-01 & T-06 to be changed to Circular Top mounting for better perfomance & Maintenance
ii | Dosage control for all dosing pumps in respect to input quality
iii | Instrumentation:- Display & Control
iv | Flow Meters missing at many places
2 | ETP | KLD
i | Heavy Metal Waste water | 207 | Input Characterstics
ii | High con Phosphrous Waste water | 642 | Source & Input Characterstics
iii | Comprehensive Waste water | 741 | Input Characterstics
iv | VI Cleaning Water | 505 | Source & Input Characterstics
v | Waste Liquid minimization | 65 | Input Characterstics
vi | Organic Waste water | 2759 | Source & Input Characterstics
vii | Zero Liquid Discharge system | 5620 | Source & Input Characterstics
viii | Volume & Treatment scheme for the Coolents from Machinaries
ix | Methods to control the Dosage according to Input Characterstics
x | Water requirement for Cooling Tower & the Source
xi | Aquastic hood for Blowers & AODP Pumps as per TNPCB Norms
xii | Laboratory equipments as per NABL Norms
3 | STP
i | Rectangular tank with Submerged Scrapper- T-02 -A/B to be changed to Circular Top mounting for better perfomance & Maintenance
ii | Belt Filter Press to Screw Press for better perfomance & Maintenace
iii | Instrumentation:- Display & Control
iv | Flow Meters missing at many places

## Addition & Deletion
| Addition | Deletion | Change of Spec
ETP | 241 | 21
WTP | 3 | 3 | 14
STP
DM

## Long Lead Items
Long Lead Items
Sr No | Long Lead Items | Submission of TDS in days | Approval on TDS | Manufacturing clearance | Lead time in days | Custom & Shipment clearance in days | Delivery on Site | PROJECT TOTAL QTY | UNITS
1 | MVR | 7 |  |  | 150
2 | MBR | 4 |  |  | 120
3 | Cryogenic | 7 |  |  | 120
4 | Submersible Mixers | 5 |  |  | 90
5 | Air Suspension Blowers | 5 |  |  | 120
6 | Recycling Mixer ( Surmersible type) with inventor | 7 |  |  | 120
7 | Bio Cord | 7 |  |  | 120
Required Immediately for Construction
1 | Foundation Bolts
2 | Puddle Flanges
3 | Sleeves